## Sheet1
Audit Report in Crusher area Ac Motor
Sr.No. | Motor Location | Motor kw | Motor Covering | Dust in Terminal Box | Cable selection and Routing | Earthing Motor | Contactor Capacity | MCCB | Overload Relay set | Panel room Dust | Panel Heat | Preventive Maintenance | Checksheet
1 | Impact ( Big) | 50 | not ok | yes | Not ok | ok | 3tf51,3tf47,3tf47 | 250A | 50A | Not ok | Not ok | Not Done | NO
2 | Impact ( small) | 37 | not ok | yes | Not ok | Not ok | 3tf47 | NO | 68A | Not ok | Not ok | Not Done | NO
3 | Impact ( small) | 30 | not ok | yes | Not ok | Not ok | 3tf46 | NO | 60A | Not ok | Not ok | Not Done | NO
4 | java | 37 | not ok | yes | Not ok | ok | 3tf47 | NO | 39A | Not ok | Not ok | Not Done | NO
5 | Belt | 15 | not ok | yes | Not ok | Not ok | 3tf34 | 16A | 24A | Not ok | Not ok | Not Done | NO
6 | Hopper | 2 | not ok | yes | Not ok | Not ok | 3tf32 | 16A | 6.2A | Not ok | Not ok | Not Done | NO
7 | Magnet Sepretor | 0.75 | not ok | yes | Not ok | Not ok | 3tf32 | 16A | 6.2A | Not ok | Not ok | Not Done | NO
Following Changes Required
1 | Panel room should be dust free
2 | Panel Room Heating Issues
3 | selection of contactor is not ok for exampale 50kw motor more capacity contactor required .
4 | main Contactor,star,Delta contactor is uniform
5 | Seprate MCCB required in All motor
6 | OLR protection not ok
7 | Required cable route change with proper protection .
8 | Required Motor Terminial Box is dust free
9 | Required Motor proper covering
10 | Daily basis preventive Maintenance is must
| Motor Location |  | Impact ( Big)
| Motor kw |  | 50
| Motor Covering |  | not ok | proper motor covering
| Dust in Terminal Box |  | yes | dust proof is must
| Cable selection and Routing |  | Not ok | proper cable laying
| Earthing Motor |  | ok | ok
| Contactor Capacity |  | 3tf51,3tf47,3tf47 | MNX110 required
| MCCB |  | 250A | ok
| Overload Relay set |  | 50A | OLR set as per motor
| Panel room Dust |  | Not ok | dust proof is must
| Panel Heat |  | Not ok | Cooling system required
| Preventive Maintenance |  | Not Done | Daily
| Checksheet |  | NO | Daily